California Department of State Architect

Approval of Photo-luminescent Exit Signs

for High and Low Level Applications

From: Casey, David [David.Casey@dgs.ca.gov]
Sent: Monday, March 20, 2006 2:09 PM
To: O'Connell@ActiveSafety
Cc: Frank Dobronte
Subject: RE: DSA - approval of photoluminescent exit signs in schools

Mr. O’Connell,

Photo-luminescent exit signs are approved for use (both high and low level) and meet the requirements of CBC 1003.2.8.4 and 1003.2.8.5 according to the California State Fire Marshal’s Interpretation 04-025.  The exits signs must meet UL Standard  924 and be installed per manufacturers’ installation specifications, and provide illumination for a minimum of 90 minutes.

As long as the photo-luminescent exit signs meet UL 924 and are approved by the State Fire Marshal they will be acceptable for use by DSA FLS Plan Reviewers.

David E. Casey

Principal/Chief Fire & Life Safety

Division of the State Architect

Department of General Services

1102 Q Street, Suite 5100

Sacramento, CA 95814

Phone:  916-327-8919

Fax: 916-327-3371

david.casey@dgs.ca.gov